## Results
|  | Snughborough Initial Power (MVA) | Snughborough Circuit Rating (MVA) | Maximum Permissible Derating Factor | Snughborough Derated Power (MVA) | Exisiting HV Cable Initial Power (MVA) | Exisiting HV Cable Circuit Rating (MVA) | Maximum Permissible Derating Factor | Exisiting HV Cable Derated Power (MVA)
Chainage 685 | Summer | 206.168 | 178 | 13.66% | 189.674 | 197.956 | 195 | 1.493% | 176.181
Chainage 692 |  | 208.626 | 178 | 14.68% | 194.022 | 162.252 | 125 | 22.96% | 144.404
Chainage 1040 |  | 213.065 | 178 | 16.46% | 191.758 | 487.136 | 555 | -13.93% | 438.422
Chainage 685 | Winter | 236.061 | 219 | 7.227% | 219.537 | 224.115 | 220 | 1.836% | 201.704
Chainage 692 |  | 236.766 | 219 | 7.504% | 220.193 | 182.866 | 141 | 22.89% | 162.751
Chainage 1040 |  | 241.263 | 219 | 9.228% | 219.549 | 553.401 | 555 | -0.2889% | 503.595
Snughborough-Corduff
|  | Initial Power (MVA) | Circuit Rating (MVA) | Maximum Permissible Derating Factor | Derated Power (MVA) | Above/Below Circuit Rating (MVA) | Derating Pecentage
Chainage 685 | Summer | 206.168 | 178 | 13.66% | 189.674 | 11.674 | 8%
Chainage 685 (RE) [4m deep] |  | 196.981 | 178 | 9.636% | 189.101 | 11.101 | 4%
Chainage 685 (RE) [3.05m deep] |  | 203.729 | 178 | 12.63% | 191.505 | 13.505 | 6%
Chainage 692 |  | 208.626 | 178 | 14.68% | 194.022 | 16.022 | 7%
Chainage 1040 |  | 213.065 | 178 | 16.46% | 191.758 | 13.758 | 10%
Chainage 685 | Winter | 236.061 | 219 | 7.227% | 219.537 | 0.537 | 7%
Chainage 685 (Re) [Snugh 80°C] |  | 219.104 | 219 | 0.04747% | 192.812 | -26.188 | 12%
Chainage 685 (RE) [4m deep] |  | 224.63 | 219 | 2.506% | 215.644 | -3.356 | 4%
Chainage 685 (RE) [3.05m deep] |  | 231.832 | 219 | 5.535% | 220.25 | 1.25 | 4.996%
Chainage 685 (RE) [Snugh @ 60°C Bentonite] |  | 219.104 | 219 | 0.04747% | 205.958 | -13.042 | 6%
Chainage 692 |  | 236.766 | 219 | 7.504% | 220.193 | 1.193 | 7%
Chainage 1040 |  | 241.263 | 219 | 9.228% | 219.549 | 0.549 | 9%
Existing High Voltage Cable Installations
|  | Initial Power (MVA) | Circuit Rating (MVA) | Maximum Permissible Derating Factor | Derated Power (MVA) | Above/Below Circuit Rating (MVA) | Derating Pecentage
Chainage 685 | Summer | 197.956 | 195 | 1.493% | 176.181 | -18.819 | 11%
Chainage 685 (RE) [4m deep] |  | 197.956 | 195 | 1.493% | 188.058 | -6.942 | 5%
Chainage 685 (RE) [3.05m deep] |  | 197.956 | 195 | 1.493% | 184.099 | -10.901 | 7%
Chainage 692 |  | 162.252 | 125 | 22.96% | 144.404 | 19.404 | 11%
Chainage 1040 |  | 487.136 | 555 | -13.93% | 438.422 | -116.578 | 10%
Chainage 685 | Winter | 224.115 | 220 | 1.836% | 201.704 | -18.296 | 10%
Chainage 685 (Re) [Snugh 80°C] |  | 224.115 | 220 | 1.836% | 206.186 | -13.814 | 8%
Chainage 685 (RE) [4 m deep] |  | 224.115 | 220 | 1.836% | 212.909 | -7.091 | 5%
Chainage 685 (RE) [3.05m deep] |  | 224.115 | 220 | 1.836% | 208.427 | -11.573 | 7%
Chainage 685 (RE) [Snugh @ 60°C Bentonite] |  | 224.115 | 220 | 1.836% | 215.151 | -4.849 | 4%
Chainage 692 |  | 182.866 | 141 | 22.89% | 162.751 | 21.751 | 11%
Chainage 1040 |  | 553.401 | 555 | -0.2889% | 503.595 | -51.405 | 9%

## IecExample
Description | Symbol | Unit | Cable1 | Cable2
Chaining | - | - | 1 | 1
Cable Type (Voltage) | V | kV | 10 | 132
Number of Cores | n | - | 1 | 3
Conductor Material | - | - | Copper | Copper
Conductor Electrical Resistivity | ρ | Ω.m | 1.7241e-08 | 1.7241e-08
Conductor Thermal Resistivity | ρcr | k.m/W | 0.0026 | 0.0026
Temperature Coefficient | per K | per K | 0.00393 | 0.00393
Formation | - |  | Flat | Trefoil
Number of Heat Sources | - | - | 3 | 1
Cross Sectional Area of Conductor | A | mm2 | 300 | 400
Maximum Permissable Temperature | θmax | ⁰C | 90 | 85
Current Rating of Isolated Cable | I | A | 665 | 585
Conductor Resistance at θmax | R | Ω/m | 7.81e-05 | 6.15e-05
Loss Factor for Sheath/Screen | λ1 | - | 0.089 | 0.135
Loss Factor for Armour | λ2 | - | 0 | 0
Thermal Resistance of Insulation | T1 | k.m/W | 0.214 | 0.835
Thermal Resistance of Armour | T2 | k.m/W | 0 | 0
Thermal Resistance of Jacket/Sheath | T3 | k.m/W | 0.104 | 0.09
External Thermal Resistance | T4 | k.m/W | 1.427 | 0.445
Conductor Losses per Core | Wc | W/m | 34.5378 | 21.0468
Dielectric Losses per Core | Wd | W/m | 0 | 2.01
Sheath Losses per Core | Ws | W/m | 3.0739 | 2.8413
Armour Losses per Core | Wa | W/m | 0 | 0
Total Losses per Core | Wh | W/m | 37.6116 | 25.8982
Spacing between Cables | S | m | 0.072 | 0
Laying Depth | L | m | 1.2 | 0.9
Crossing Angle | B | Radians | 1.57 | 1.57
Backfill Resistivity | ρsoil | k.m/W | 0.8 | 0.8
Ambient Temperature | θa | °C | 25 | 25